## README
PRELIMINARY — SCREENING ONLY, NON-DECISION-GRADE (revised per technical review)
Base case now excludes LCFS, IRA 45V, CCS and $/kg offtake revenue (all behind explicit toggles in Global_Assumptions); H2 energy basis is LHV-consistent; NPV is reported incremental to the 0% baseline. See the Corrections_Log and Validation_Tests sheets. Do NOT use LCOH/NPV/abatement figures for investment decisions or cross-site ranking.
HARMONIZED H2 TEA + RELIABILITY MODEL — PG&E
PG&E Transmission System — Graniterock Industrial Use Case
Harmonization note | This workbook is one of five case studies built on a single harmonized template. The Global_Assumptions sheet, all formulas, the PoF thresholds (FCGR multipliers, base leak/burst rates, 20-yr horizon) and the inspection/maintenance unit costs are IDENTICAL across every case study. Only the Component_Register and system parameters differ by configuration.
System type | Transmission pipeline
End use | Graniterock asphalt batch plant (industrial)
Operating / native pressure | 390 psig (~26.9 bar)
Pipe / lateral | X60, 20-in OD, 0.375-in WT, MOP 1400 psi, 100 mi, 14 segment(s)
SHEET INDEX
1. README | This sheet
2. Global_Assumptions | Shared inputs — IDENTICAL across all case studies (blue = master inputs)
3. Component_Register | System-specific components and counts
4. Reliability_Inputs | OREDA failure-mode rates (LB/mean/UB) per component
5. H2_Effect | Hydrogen amplification by pressure band + FCGR multipliers (thresholds)
6. Failure_Rates | PoF(20yr)=1-EXP(-rate*8760*horizon) — base & H2
7. Pipe_Integrity | Fracture-mechanics pipe PoF vs blend (FCGR thresholds)
8. PoF_Summary | Component-level PoF20 with amber/red flags (harmonized thresholds)
9. Inspection_Maint | I&M plan; common-pipe unit costs from Global_Assumptions
10. Blend_Properties | Volume→energy fraction, flow factor, H2 demand (kg/yr) by blend
11. TEA_CAPEX | Retrofit/new pipeline, injection/compression, storage, CCS/NCD
12. TEA_Hydraulics | Pressure drop & compressor count, near vs 100-mi injection
13. TEA_OPEX_Perf | Energy, O&M, inspection, losses + performance metrics
14. TEA_Network | Production / transmission / delivery cost allocation
15. TEA_Levelized | LCOH, $/tCO2e avoided, levelized carbon-capture cost
16. TEA_Pathways | Retrofit vs new; blend vs full; direct vs carrier (high-level)
17. Scenario_Results | Unified blend × distance × pathway sweep (formula-driven)
18. Lifecycle_50yr | 50-yr reliability lifecycle: PoF/TTF, inspection & maintenance downtime → derived availability
19. Fuel_Cost | NG + H2 blended fuel cost by blend (combustion end uses; 0 for transmission)
20. Cashflow_50yr | Detailed 50-year cashflow for a selectable scenario (blend/injection/pathway) + NPV
21. NPV_Comparison | NPV across blend, pressure, pathway, and injection point
22. Use_Case_Summary | Compiled cost breakdown, drivers, feasibility thresholds
Colour key
Blue = hardcoded input | Black = formula/derived
Green = cross-sheet reference

## Global_Assumptions
GLOBAL ASSUMPTIONS — shared across all harmonized case studies
IDENTICAL in every workbook. Blue = master input. Change here to propagate everywhere.
Parameter | Value | Unit | Source / note
A. ECONOMIC BASIS
Capital cost recovery factor (CCRF) | 0.14 | fraction | [P1][P2] DOE H2A
CCRF (on-site electrolysis) | 0.15 | fraction | [P2]
Utility discount rate | 0.08 | fraction | [P3]
Hurdle rate (blended) | 0.0575 | fraction | [P3]
Inflation de-escalator | 0.025 | fraction | [P2]
Project economic life / lifecycle horizon | 50 | years | 50-yr lifecycle
System availability (derived prior; see Lifecycle_50yr) |  | fraction | Derived 50-yr mean from Lifecycle_50yr (single availability series). [corrected]
B. PRICES & CARBON VALUE
RH2 commodity cost (base) | 2 | $/kg | [P1][P2]
RH2 commodity (low) | 1.5 | $/kg | [P1]
RH2 commodity (high) | 3 | $/kg | [P1]
Natural gas price 2025 | 4.74 | $/GJ (UCI $5/MMBtu) | [P3]
Natural gas price 2050 | 4.39 | $/GJ | [P3]
Grid renewable electricity | 235 | $/MWh (UCI blended $0.235/kWh) | [P2]
Electricity unit cost |  | $/kWh | from elec_mwh/1000
LCFS carbon credit |  | $/credit | Gated: 0 unless LCFS eligible=1 (then LCFS price). [corrected]
IRA 45V PTC (levelized reduction) |  | $/kg | Gated: 0 unless 45V eligible=1. [corrected]
C. PHYSICAL CONSTANTS
H2 higher heating value | 39.4 | kWh/kg | physical
H2 lower heating value | 33.3 | kWh/kg | physical
H2 energy content |  | GJ/kg | LHV-consistent: LHV_kWh*0.0036 GJ/kg (was 0.113745, ~5.4% low). [corrected]
H2/NG volumetric energy ratio (k) | 0.336 | - | physical
CO2 displaced per kg zero-C H2 | 7.13 | kgCO2/kg | derived
H2 GWP100 (leakage CO2e) | 11.6 | - | [R7] Sand 2023
H2 leakage fraction (base) | 0.005 | fraction | [R7][U2]
D. CCS & NOx CAPTURE/DESTRUCTION
CO2 capture fraction |  | fraction | Gated: capture only when CCS enabled=1 -> no scenario charged CCS in base. [corrected]
CCS unit cost - industrial | 60 | $/tCO2 | [P3] Tbl 3
CCS unit cost - power gen | 90 | $/tCO2 | [P3] Tbl 3
CCS unit cost - DAC | 225 | $/tCO2 | [P3] Tbl 3
NCD (SCR) base cost @0% blend | 8 | $/tCO2e | [U2] placeholder
NCD additional per unit blend | 6 | $/tCO2e | [U2] placeholder
E. COMPRESSION & HYDRAULICS
Compression energy | 3.1 | kWh/kg | [R4] DOE avg
Compressor CAPEX | 0.75 | $M/MW | MDPI 2026
Compressor efficiency | 0.75 | fraction | [R4]
Compressor maintenance | 0.03 | frac CAPEX/yr | [R4] DOE
Compressor station spacing | 60 | miles | [R3] HyBlend
F. CAPEX UNIT COSTS
New purpose-built pipeline | 4 | $M/mile | [P3]
Retrofit/repurpose factor | 0.2 | fraction | [P3][R5] EHB
New H2 pipe premium vs NG | 1.3 | multiplier | [R5]
Injection+metering+control skid | 2 | $M/point | [P2]
On-site storage CAPEX | 265 | $/kg | [P2] Reed 2024
Storage buffer duration | 1 | days | [U2]
Pipeline O&M | 0.012 | frac CAPEX/yr | [R5] EHB
G. RELIABILITY / PoF THRESHOLDS
PoF assessment horizon | 20 | years | harmonized
Pipe base annual leak rate | 1e-06 | /hr | screening anchor
Pipe base annual burst rate | 5e-08 | /hr | screening anchor
PoF amber threshold | 0.3 | fraction | harmonized flag
PoF red threshold | 0.6 | fraction | harmonized flag
H. INSPECTION & MAINTENANCE UNIT COSTS (common pipe)
Inspection - normal pipeline | 52361 | $/mile/yr | blended ILI/HT/DA
Inspection - purpose-built | 26180 | $/mile/yr | less frequent
ILI frequency | 7 | years | PHMSA
ILI cost | 33450 | $/mile | NPV 5%
I. LIFECYCLE, FUEL & CASHFLOW (50-year extension)
Lifecycle / cashflow horizon | 50 | years | 50-yr extension
Combustion-efficiency gain per 100% blend (Thermoflex) | 0.01 | fraction (+=gain; Thermoflex) | screening [R13]
Storage O&M (annual % of CAPEX) | 0.02 | frac CAPEX/yr | [P2]
H2 production value (generation revenue) |  | $/kg | Gated: 0 unless offtake revenue enabled=1 (avoids double counting). [corrected]
Delivered NG retail tariff (transport revenue) | 8 | $/GJ | [P3] retail
IRA 45V credit magnitude (revenue) |  | $/kg | Gated: 0 unless 45V eligible=1; capped at 45V duration years in cashflow. [corrected]
FCGR multiplier by blend (pipe PoF threshold)
Blend % | FCGR mult
0 | 1
5 | 6
10 | 8
20 | 10
30 | 10
50 | 10
75 | 10
100 | 10
J. SCENARIO TOGGLES & POLICY ELIGIBILITY (review corrections)
CCS enabled (1=on, 0=off) | 0 | switch | [review scenario lever]
LCFS eligible (1=yes, 0=no) | 0 | switch | [review scenario lever]
LCFS price if eligible | 66 | $/tCO2e | [review scenario lever]
IRA 45V eligible (1=yes, 0=no) | 0 | switch | [review scenario lever]
IRA 45V credit duration | 10 | years | [review scenario lever]
H2 offtake/production revenue enabled (1/0) | 0 | switch | [review scenario lever]
Note on B11: Review fix #9: LCOH previously used a fixed 0.97 while cashflow used the derived ~0.955. Now both use the derived series.
Note on B20: Review fix #1.2: base case $0. LCFS is a transport-fuel program; stationary eligibility must be documented before switching on.
Note on B25: Review fix #4 (units): 33.3 kWh/kg x 0.0036 = 0.11988 GJ/kg. The previous hardcoded 0.113745 was ~5.4% too low and inflated H2 mass demand.
Note on B31: Review fix #3: CCS was charged in every blend incl. 0%. Now an explicit option.
Note on B66: Review fix #1.3: an end user cannot pay for H2 as fuel AND book $/kg production revenue. Base OFF; use avoided-cost framing / incremental NPV.
Note on B68: Review fix #1.1: 45V accrues to the qualified producer for 10 years, not the end user for 50. Base OFF.
Note on B82: CCS is now an explicit option. Base case OFF, so no scenario is charged CCS.
Note on B83: Stationary CHP/kiln/transport LCFS eligibility is unproven -> base OFF.
Note on B84: CARB weekly avg ~$66/t (was $150). Only used when LCFS eligible=1.
Note on B85: 45V is earned by the qualified H2 PRODUCER, not the end user -> base OFF.
Note on B86: 45V statutory credit period is 10 years, not 50.
Note on B87: End users purchase and consume H2; they cannot also book $/kg production revenue. Base OFF.

## Component_Register
COMPONENT REGISTER — PG&E
System-specific components. Reliability and I&M layers act on these.
Component | Count | Class | Pressure (psig) | Note
Pipeline Segment | 14 | pipe | 390 | in inspection/maintenance register
Gate Valve | 15 | valve | 390 | in inspection/maintenance register
Pressure Regulator | 3 | regulator | 390 | in inspection/maintenance register
Meter | 3 | meter | 390 | in inspection/maintenance register
Centrifugal Compressor | 1 | compressor | 390 | in inspection/maintenance register

## Reliability_Inputs
RELIABILITY INPUTS — OREDA failure-mode rates
Blue = OREDA hardcoded rates (identical per component type across all case studies).
Component | Failure mode | FM | Rate LB (/hr) | Rate mean (/hr) | Rate UB (/hr) | H2 mult | Source
Gate Valve | Abnormal instrument reading | AIR | 2.59e-06 | 1.69e-05 | 4.17e-05 |  | OREDA valve
Gate Valve | External leakage | EL | 2.38e-07 | 8.11e-06 | 2.77e-05 |  | OREDA valve
Gate Valve | Minor in-service problems | SER | 3.04e-06 | 2.58e-05 | 6.73e-05 |  | OREDA valve
Pressure Regulator | Abnormal instrument reading | AIR |  | 2.14e-07 |  | 1 | OREDA regulator
Pressure Regulator | Delayed operation | DEL |  | 4.03e-07 |  | 1 | OREDA regulator
Pressure Regulator | External leakage | EL |  | 3.68e-07 |  | 1 | OREDA regulator
Pressure Regulator | Internal leakage | IL |  | 9.99e-07 |  | 1 | OREDA regulator
Pressure Regulator | Minor in-service problems | SER |  | 7.6e-07 |  | 1 | OREDA regulator
Pressure Regulator | Spurious operation | SPO |  | 8.95e-08 |  | 1 | OREDA regulator
Pressure Regulator | Structural deficiency | STR |  | 2.34e-07 |  | 1 | OREDA regulator
Pressure Regulator | Pressure control failure | PCT |  | 7.31e-07 |  | 1 | OREDA regulator
Meter | Abnormal instrument reading | AIR |  | 2.26e-05 |  | 1 | NGRMS meter
Centrifugal Compressor | Abnormal instrument reading | AIR |  | 7.18e-05 |  | 1 | OREDA compressor
Centrifugal Compressor | Breakdown/overheating | BRD |  | 6.07e-06 |  | 1 | OREDA compressor
Centrifugal Compressor | External leakage | EL |  | 5.35e-05 |  | 1 | OREDA compressor
Centrifugal Compressor | Fail to start | FTS |  | 9.72e-06 |  | 1 | OREDA compressor
Centrifugal Compressor | Internal leakage | IL |  | 1.37e-05 |  | 1 | OREDA compressor
Centrifugal Compressor | Output issues | OUT |  | 2.29e-05 |  | 1 | OREDA compressor
Centrifugal Compressor | Parameter deviation | PDE |  | 3.33e-05 |  | 1 | OREDA compressor
Centrifugal Compressor | Minor in-service problems | SER |  | 4.47e-05 |  | 1 | OREDA compressor
Centrifugal Compressor | Spurious stop | UST |  | 2.61e-05 |  | 1 | OREDA compressor
Centrifugal Compressor | Vibration | VIB |  | 2.56e-05 |  | 1 | OREDA compressor
Centrifugal Compressor | Structural deficiency | STR |  | 2.41e-06 |  | 1 | OREDA compressor

## H2_Effect
HYDROGEN EFFECT — amplification by pressure band + FCGR thresholds
Applied band selected by native pressure (26.9 bar). Amplification = applied%/No-H2%.
Native pressure (bar) | 26.9
FM | Failure mode | No-H2 % | 0-5 bar % | 5-20 bar % | 20-100 bar % | Applied % | Amplification
AIR | Abnormal instrument reading | 4.3 | 4.3 | 4.3 | 4.3
DEL | Delayed operation | 12.5 | 32.9 | 62.5 | 67.5
EL | External leakage | 12.3 | 29.6 | 48.8 | 57.6
FTC | Fail to close | 15.8 | 25.9 | 42.5 | 47.8
FTO | Fail to open | 19.1 | 34.7 | 51.1 | 61.2
IL | Internal leakage | 4.4 | 8.3 | 19.4 | 13.9
VLC | Valve leakage in closed pos. | 13.1 | 29.1 | 48.1 | 55.8
SER | Minor in-service problems | 8.9 | 13.7 | 15 | 16.9
SPO | Spurious operation | 1.8 | 1.8 | 1.8 | 1.8
STR | Structural deficiency | 9.3 | 26.6 | 43.8 | 54.5
FCGR multipliers (pipe-body fatigue) — see Global_Assumptions

## Failure_Rates
FAILURE RATES, MTTF & 20-YEAR PoF
PoF(20yr)=1-EXP(-rate*8760*horizon). Horizon and basis from Global_Assumptions.
Component | Failure mode | FM | Mean rate (/hr) | H2 mult | H2 rate (/hr) | MTTF (yr) | PoF20 base | PoF20 H2

## Pipe_Integrity
PIPE-BODY INTEGRITY SCREENING — PG&E
X60: 20-in OD, 0.375-in WT. FCGR mult & base rates from Global_Assumptions (harmonized thresholds).
Flaw length-to-depth ratio | 15
SMYS (psi) | 72000
KIC (MPa.m^0.5) | 110
OD (in) | 20
WT (in) | 0.375
MOP (psi) | 1400
Stress ratio R | 0.92
Pressure cycles/yr | 10000
Avg crack depth (in) | 0.035
Steel grade | X60
Base annual leak rate (/hr)
Base annual burst rate (/hr)
Blend % | FCGR mult | Leak rate H2 (/hr) | Burst rate H2 (/hr) | PoF leak 20yr | PoF burst 20yr | Combined PoF 20yr
0
5
10
20
30
50
75
100

## PoF_Summary
COMPONENT-LEVEL 20-YEAR PoF SUMMARY (harmonized thresholds)
Series-logic fault tree. PoF calibrated to UCI component Bayesian-network models (100k MC) + UCI turbine model. Amber/red flags from Global_Assumptions.
Component | Count | Approach | PoF20 base | PoF20 H2 | Flag | Dominant hydrogen effect
Pipeline Segment | 14 | Fracture-mechanics fatigue |  |  |  | FCGR up ~1 order of magnitude
Gate Valve | 15 | UCI valve BN (100k MC) | 0.6189 | 0.6795 |  | EL & delayed-op amplified
Pressure Regulator | 3 | UCI regulator BN (100k MC) | 0.8537 | 0.8716 |  | Seal/diaphragm compatibility
Meter | 3 | NGRMS MTTF (instrument) |  |  |  | Gas-property change affects calibration
Centrifugal Compressor | 1 | UCI compressor BN (100k MC) | 0.7813 | 0.7799 |  | Seal leakage; API 617 limits

## Inspection_Maint
INSPECTION & MAINTENANCE PLAN (common-pipe unit costs harmonized)
Pipe inspection unit costs come from Global_Assumptions (normal vs purpose-built), identical across cases.
Component | Inspection (type & frequency) | Maintenance | Unit cost basis | Annual cost ($)
Pipeline Segment | Patrol + ILI (>=1/7yr); leak survey | Condition-based (clamp/sleeve/replace)
Gate Valve | Functional/leak test >=1/yr | Lubricate; reseat; replace seals | component-scale (vendor) | 75000
Pressure Regulator | Visual monthly; functional 2/yr | Pilot adjust; preventive 2/yr | component-scale (vendor) | 12000
Meter | Continuous remote monitoring | Calibration/recalibration | component-scale (vendor) | 9000
Centrifugal Compressor | Continuous; semiannual; annual | Condition-based + scheduled | component-scale (vendor) | 50000
Inspection scenario (per mile)
Scenario | $/mile/yr
Normal (existing) pipeline
Purpose-built (less frequent)

## Blend_Properties
BLEND PROPERTIES & H2 DEMAND — PG&E
Energy fraction E=v·k/(v·k+1−v); flow factor=1/((1−v)+v·k); demand=fuel·E/gj_kg. k, gj_kg from Global.
Baseline fuel energy (GJ/yr) | 1826000
Baseline fossil CO2 (t/yr)
Blend % (vol) | H2 energy frac | Flow factor | FCGR mult | kg basis | H2 demand (kg/yr) | CO2 avoided (t/yr) | Residual CO2 (t/yr)
0
5
10
20
30
50
75
100

## TEA_CAPEX
CAPEX MODEL — PG&E
Unit costs from Global_Assumptions. Pipe length is system length (transmission) or lateral distance (end-use).
Pipeline option | $/mile | Total ($) | Basis
New purpose-built |  |  | new_pipe×premium [P3][R5]
Repurposed (retrofit) |  |  | new_pipe×retrofit_factor [P3]
Injection / compression / storage
Item | Value | Unit | Basis
Injection+metering+control skid |  | $ | [P2]
Storage (buffer) |  | $ @100% demand | storage_days×kg [P2]
Compressor unit CAPEX |  | $/unit @100% | comp_capex×MW
CCS & NCD (carbon)
Item | $/tCO2
CCS industrial
CCS power generation
CCS DAC
NCD base / slope

## TEA_Hydraulics
HYDRAULICS & COMPRESSOR COUNT — PG&E
N_comp = MAX(1, CEILING(distance/spacing × flow_factor)). Spacing from Global_Assumptions.
Near distance (mi) | 10 |  | Far distance (mi) | 100
Blend % | Flow factor | Compressors near | Compressors far | Comp power near (MW) | Comp energy (kWh/kg)
0
5
10
20
30
50
75
100

## TEA_OPEX_Perf
OPEX & TECHNICAL PERFORMANCE — PG&E
Energy fraction, flow factor & demand from Blend_Properties; inspection from Global I&M unit cost × miles.
Blend % | Energy frac | Delivery eff. | Compression ($/yr) | Inspection ($/yr) | Leakage make-up (kg/yr) | Throughput flag
0
5
10
20
30
50
75
100

## TEA_Network
NETWORK-BASED COST ALLOCATION — PG&E
Production / transmission / delivery split. Validated pipeline anchor from Reed 2024 [P2].
Cost layer | $/kg | Output metric | Basis
Production (RH2 commodity) |  | $/kg produced | [P1][P2]
Transmission (pipeline+compression) | 0.71 | $/kg transported | [P2] Reed 2024
Local delivery (skid+storage) | 0.11 | $/kg delivered | [P2]
End-use integration | 0.04 | $/MWh useful | [P2]
Total delivered, $/kg (excl. $/MWh integration) |  | $/kg | validated $2.85/kg [P2]
Alternative delivery pathways ($/kg)
Pathway | $/kg | Type | Source
Pipeline (direct) | 2.85 | direct | [P2]
Cryo-tanker (direct) | 3.98 | direct | [P2]
On-site electrolysis | 3.65 | on-site | [P2]
Ammonia carrier | 5 | carrier | placeholder
LOHC carrier | 4.5 | carrier | placeholder
Note on B7: Units are $/MWh useful — reported separately, never summed into the $/kg total.
Note on B8: Review fix #11.1/11.2: end-use integration is $/MWh and cannot be added to $/kg layers. Stale cached total also refreshed on recalc.

## TEA_Levelized
LEVELIZED METRICS — PG&E
LCOH = RH2 + (CCRF·CAPEX + OPEX)/(demand·availability). Pulls scenario totals from Scenario_Results (near retrofit).
Blend % | LCOH near ($/kg) | LCOH far ($/kg) | LCOH w/ 45V (if eligible) ($/kg) | $/tCO2e avoided | Lev. capture ($/tCO2) | CO2 avoided (t/yr)
0
5
10
20
30
50
75
100
Note on D3: Only differs from LCOH when 45V eligible=1 in Global_Assumptions.
Note on B4: Review fix: at 0% H2 there is no hydrogen -> LCOH is N/A (not 0 or -$1.35/kg).

## TEA_Pathways
COMPARATIVE PATHWAYS (high level) — PG&E
Retrofit vs new; blend vs full; direct vs carrier. Paper-sourced where available; carriers are placeholders.
Comparison | Value | Unit | Note
Retrofit pipeline |  | $ total | 20% of new [P3]
New purpose-built pipeline |  | $ total | new×premium [R5]
Blend 20% (near) LCOH |  | $/kg | moderate decarbonization
Full 100% (near) LCOH |  | $/kg | max decarbonization
Pipeline (direct) |  | $/kg | [P2]
Cryo-tanker (direct) |  | $/kg | [P2]
On-site electrolysis |  | $/kg | [P2]
Ammonia carrier |  | $/kg | placeholder
LOHC carrier |  | $/kg | placeholder

## Scenario_Results
UNIFIED SCENARIO RESULTS — PG&E (formula-driven)
Blend × distance × pathway. All columns computed from Global_Assumptions + Blend_Properties + Hydraulics.
Blend% | Dist(mi) | Pathway | H2 (kg/yr) | Compr. | Pipe CAPEX($) | Comp CAPEX($) | Skid+Stor($) | Ann.CAPEX($) | Ann.OPEX($) | LCOH($/kg) | CCS($/yr) | $/tCO2e | Lev.cap($/tCO2)
0 |  | retrofit
0 |  | retrofit
0 |  | new
5 |  | retrofit
5 |  | retrofit
5 |  | new
10 |  | retrofit
10 |  | retrofit
10 |  | new
20 |  | retrofit
20 |  | retrofit
20 |  | new
30 |  | retrofit
30 |  | retrofit
30 |  | new
50 |  | retrofit
50 |  | retrofit
50 |  | new
75 |  | retrofit
75 |  | retrofit
75 |  | new
100 |  | retrofit
100 |  | retrofit
100 |  | new

## Lifecycle_50yr
50-YEAR LIFECYCLE & DERIVED AVAILABILITY — PG&E
PoF rises with age and resets at condition-based maintenance (when an inspection finds PoF>threshold). Availability is DERIVED from inspection + maintenance + expected-failure downtime over the 50-yr horizon (not an input).
Class | Count | Insp int (yr) | Thr | MTTR (h) | Insp down (h) | Insp $/event | Maint $/event | PoF20 H2 | lambda (/hr) | MTTF (yr) | Tau_thr (yr) | Maint int M (yr) | #Insp 50yr | #Maint 50yr | Failure h/yr | Downtime 50yr (h) | Gen | CO2 | (1-PoF)^n
pipe | 14 | 7 | 0.3 | 240 | 24 | 33450 | 150000 | [9 empty] | 0 | 0
valve | 15 | 2 | 0.3 | 24 | 4 | 1500 | 8000 | [9 empty] | 0 | 0
regulator | 3 | 3 | 0.3 | 16 | 3 | 1200 | 6000 | [9 empty] | 0 | 0
meter | 3 | 2 | 0.3 | 8 | 2 | 800 | 4000 | [9 empty] | 0 | 0
compressor | 1 | 1 | 0.3 | 168 | 24 | 12000 | 60000 | [9 empty] | 0 | 0
SYSTEM ROLL-UP (derived from the table above)
Total downtime over 50 yr (h)
Average annual downtime (h)
DERIVED AVAILABILITY (50-yr mean)
System PoF20 (series)
System MTTF (series, yr)
Avg inspection cost ($/yr)
Avg maintenance cost ($/yr)
#Maint over 50 yr is 0 where the component's PoF never reaches the maintenance threshold within the horizon (M > 50).

## Fuel_Cost
BLENDED FUEL COST — PG&E
Fuel = (NG portion + H2 portion)/combustion-efficiency. THERMOFLEX-VALIDATED: LHV efficiency RISES slightly with H2 (Sol Titan +1.0%, C65/C200 +0.19%), so eff=1+gain*(blend/100) — the earlier 3% derate is rejected. Gross (availability applied in Cashflow_50yr).
Blend % | H2 energy frac | Comb. eff. | Fuel NG ($/yr) | H2 production ($/yr) | Total fuel ($/yr)
0 |  |  | 0 | 0 | 0
5 |  |  | 0 | 0 | 0
10 |  |  | 0 | 0 | 0
20 |  |  | 0 | 0 | 0
30 |  |  | 0 | 0 | 0
50 |  |  | 0 | 0 | 0
75 |  |  | 0 | 0 | 0
100 |  |  | 0 | 0 | 0

## Thermoflex_Validation
THERMOFLEX THERMODYNAMIC VALIDATION & FUEL-SYSTEM CONSTRAINTS
GT PRO/Thermoflex simulation of the UCI turbines (Sol Titan 130, Capstone C65/C200) over 0->100% H2. Validates the model's thermodynamic assumptions and sets fuel-system hardware constraints.
A. Validated thermodynamic relationships
Quantity | NG (0%) | 50% H2 | 100% H2 | Trend | Source & formula
Fuel volumetric flow (÷NG) | 1.00x | 1.54x | 3.39x | RISES | Thermoflex fit VF=1/((1-v)+0.295v)
Fuel mass flow | 1.00x | ~0.79x | ~0.38x | falls | H2 has lower mass per unit energy
Gross LHV efficiency (turbine) | 33.05% | ~33.4% | 33.88% | +1.0% | Thermoflex Sol Titan 130
Gross LHV efficiency (microturbine) | 41.68% | ~41.70% | 41.76% | +0.19% | Thermoflex C65/C200
Exhaust CO2 mol% | 1.86% | 1.39% | 0.000% | falls to ~0 | CO2=1.861*(1-Efrac)
Sol Titan gross power | 13.29 MW | ~13.5 MW | 13.88 MW | RISES | constant TIT 1422K
Turbine outlet temp (TOT) | 768.3 K | ~766 K | 764.2 K | falls <10K | within limit
B. Fuel-system hard constraints (Thermoflex + UCI operator-confirmed)
Constraint | Trigger | Threshold | Replacement CAPEX |  | Basis
Transmission system — transports the blend, does not combust it. No fuel-system constraints; H2 limits are pipe/valve partial-pressure (see PoF_Summary & Global).
Note: efficiency values applied harmonized at +1.0%/100% in Global_Assumptions B64; microturbine actual +0.19% (sub-1% fuel-cost effect). CAPEX are screening placeholders pending OEM quotation.

## Cashflow_50yr
DETAILED 50-YEAR CASHFLOW — PG&E (selectable scenario)
Change the blue controls to switch scenario. Capital is taken in year 1; inspection & maintenance follow the lifecycle schedule; fuel, revenue and credits scale with the derived per-year availability. Discounted at the utility rate over 50 years.
Scenario (1=near-retrofit, 2=far-retrofit, 3=far-new) | 1 |  | H2 demand (kg/yr) |  |  | Comp CAPEX ($)
Blend % (vol) | 20 |  | H2 energy fraction |  |  | Skid+storage ($)
Injection |  |  | CO2 avoided (t/yr) |  |  | Compressors
Pathway |  |  | Delivered energy (GJ/yr) |  |  | Total CAPEX ($)
Selected distance (mi) |  |  | Combustion efficiency |  |  | Storage CAPEX ($)
Blend index |  |  | Pipe CAPEX ($) |  |  | Pressure adder ($/kg) | 0.15
Annual O&M constants
Compression elec ($/yr)
Compressor maint ($/yr)
Pipe O&M ($/yr)
Pressure O&M ($/yr)
Storage O&M ($/yr)
Year | Avail. | CAPEX ($) | Inspect ($) | Maint ($) | Fuel NG ($) | H2 prod ($) | Stor O&M ($) | O&M/Compr ($) | Revenue ($) | Carbon cr ($) | Net ($) | Disc. net ($)
1 |  |  |  |  | 0 | 0 |  |  |  | 0
2 |  |  |  |  | 0 | 0 |  |  |  | 0
3 |  |  |  |  | 0 | 0 |  |  |  | 0
4 |  |  |  |  | 0 | 0 |  |  |  | 0
5 |  |  |  |  | 0 | 0 |  |  |  | 0
6 |  |  |  |  | 0 | 0 |  |  |  | 0
7 |  |  |  |  | 0 | 0 |  |  |  | 0
8 |  |  |  |  | 0 | 0 |  |  |  | 0
9 |  |  |  |  | 0 | 0 |  |  |  | 0
10 |  |  |  |  | 0 | 0 |  |  |  | 0
11 |  |  |  |  | 0 | 0 |  |  |  | 0
12 |  |  |  |  | 0 | 0 |  |  |  | 0
13 |  |  |  |  | 0 | 0 |  |  |  | 0
14 |  |  |  |  | 0 | 0 |  |  |  | 0
15 |  |  |  |  | 0 | 0 |  |  |  | 0
16 |  |  |  |  | 0 | 0 |  |  |  | 0
17 |  |  |  |  | 0 | 0 |  |  |  | 0
18 |  |  |  |  | 0 | 0 |  |  |  | 0
19 |  |  |  |  | 0 | 0 |  |  |  | 0
20 |  |  |  |  | 0 | 0 |  |  |  | 0
21 |  |  |  |  | 0 | 0 |  |  |  | 0
22 |  |  |  |  | 0 | 0 |  |  |  | 0
23 |  |  |  |  | 0 | 0 |  |  |  | 0
24 |  |  |  |  | 0 | 0 |  |  |  | 0
25 |  |  |  |  | 0 | 0 |  |  |  | 0
26 |  |  |  |  | 0 | 0 |  |  |  | 0
27 |  |  |  |  | 0 | 0 |  |  |  | 0
28 |  |  |  |  | 0 | 0 |  |  |  | 0
29 |  |  |  |  | 0 | 0 |  |  |  | 0
30 |  |  |  |  | 0 | 0 |  |  |  | 0
31 |  |  |  |  | 0 | 0 |  |  |  | 0
32 |  |  |  |  | 0 | 0 |  |  |  | 0
33 |  |  |  |  | 0 | 0 |  |  |  | 0
34 |  |  |  |  | 0 | 0 |  |  |  | 0
35 |  |  |  |  | 0 | 0 |  |  |  | 0
36 |  |  |  |  | 0 | 0 |  |  |  | 0
37 |  |  |  |  | 0 | 0 |  |  |  | 0
38 |  |  |  |  | 0 | 0 |  |  |  | 0
39 |  |  |  |  | 0 | 0 |  |  |  | 0
40 |  |  |  |  | 0 | 0 |  |  |  | 0
41 |  |  |  |  | 0 | 0 |  |  |  | 0
42 |  |  |  |  | 0 | 0 |  |  |  | 0
43 |  |  |  |  | 0 | 0 |  |  |  | 0
44 |  |  |  |  | 0 | 0 |  |  |  | 0
45 |  |  |  |  | 0 | 0 |  |  |  | 0
46 |  |  |  |  | 0 | 0 |  |  |  | 0
47 |  |  |  |  | 0 | 0 |  |  |  | 0
48 |  |  |  |  | 0 | 0 |  |  |  | 0
49 |  |  |  |  | 0 | 0 |  |  |  | 0
50 |  |  |  |  | 0 | 0 |  |  |  | 0
NPV (net, $)
Undiscounted net 50-yr ($)
Mean availability (50-yr)
Note on E7: Review fix #10: efficiency RISES slightly with H2 (Thermoflex), matching Fuel_Cost. Was 1-gain (a derate), inconsistent with the Fuel_Cost sheet.
Note on K17: Review fix #1.1: IRA 45V applied only in years 1..(45V duration); LCFS continues while eligible.

## NPV_Comparison
NPV COMPARISON ACROSS SCENARIOS — PG&E
Screening NPV. Lead with the INCREMENTAL column (vs the 0% fossil baseline); the 0% incremental NPV is zero by construction. Absolute NPV is retained for continuity only and is non-decision-grade (end-use benefit = avoided electricity/heat, not modelled here; transmission uses a merchant revenue proxy).
Annuity factor (50 yr) |  |  | Mean availability
A. NPV vs blend (near injection, retrofit)
Scenario | CAPEX ($) | Annual net ($/yr) | Absolute NPV 50yr ($) — non-decision-grade | Avail. | Incremental NPV vs 0% ($) — decision-relevant
0% near retrofit
5% near retrofit
10% near retrofit
20% near retrofit
30% near retrofit
50% near retrofit
75% near retrofit
100% near retrofit
B. NPV vs delivery pressure (20% blend, near retrofit)
Scenario | CAPEX ($) | Annual net ($/yr) | NPV 50yr ($) | Avail.
200 psig
390 psig
465 psig
600 psig
900 psig
1200 psig
1500 psig
C. NPV vs pathway (20% blend, far injection)
Scenario | CAPEX ($) | Annual net ($/yr) | NPV 50yr ($) | Avail.
20% far retrofit
20% far new-build
D. NPV vs injection point (20% blend, retrofit)
Scenario | CAPEX ($) | Annual net ($/yr) | NPV 50yr ($) | Avail.
20% near retrofit
20% far retrofit

## Use_Case_Summary
COMPILED TEA SUMMARY — PG&E
Cost breakdown, key drivers, tradeoffs and feasibility thresholds (20% blend, near retrofit).
System type | Transmission pipeline
End use | Graniterock asphalt batch plant (industrial)
Operating/native pressure | 390 psig
H2 demand @20% blend (kg/yr)
Delivered LCOH near @20% ($/kg)
Delivered LCOH far @20% ($/kg)
Annualized CAPEX near ($/yr)
Annual OPEX near ($/yr)
$/tCO2e avoided @20%
Levelized carbon-capture ($/tCO2)
Key economic drivers
• H2 commodity price (dominant on LCOH)
• Injection distance (near vs 100-mi compressors)
• Blend level (raises cost, lowers delivered energy)
• Utilization / demand (inverse on LCOH)
• Delivery pressure (compression cost)
• IRA 45V & LCFS credits (lower net cost)
Feasibility thresholds
Lowest cost: inject near end use, moderate blend (≤20%), lowest workable pressure, capture credits.

## Validation_Tests
MINIMUM VALIDATION TESTS (auto-checked; recalculates on open)
# | Test | Result | Basis / note
1 | Zero-blend |  | At 0% H2: demand, H2 CAPEX and CCS cost all zero.
2 | Baseline (incremental NPV=0) |  | Incremental NPV at 0% blend is zero by construction.
3 | Units (LHV consistent) |  | H2 GJ/kg equals LHV_kWh x 0.0036.
4 | Units (no $/kg + $/MWh sum) |  | Network total excludes the $/MWh integration term.
5 | Policy: 45V capped at 10 yr |  | 45V duration input = 10 years; cashflow gates 45V to years 1..10.
6 | Credit: LCFS=0 in base case |  | LCFS is zero unless eligibility toggle = 1.
7 | Hydraulic: outlet pressure OK |  | Not modelled — N_comp is a screening proxy; compressible hydraulics is future work.
8 | Availability consistency |  | LCOH and cashflow use the same derived 50-yr mean availability.
9 | Reconciliation (dashboard/report) |  | Reconcile to a single engine; SoCalGas workbook not provided in this set.
10 | Manual benchmark (0/20/100%) |  | Independently reproduce the 0%, 20% and 100% cases before quoting results.
PASS/FAIL cells recalculate when the file is opened in Excel/LibreOffice.

## Corrections_Log
CORRECTIONS APPLIED (technical review response)
PRELIMINARY / SCREENING ONLY — NON-DECISION-GRADE. These corrections fix boundary, unit, policy and consistency errors so the base case is defensible; they do not turn the suite into an investment-grade model.
Corrected in this revision
1. Units (LHV) | H2 energy content now LHV-consistent (=33.3 kWh/kg x 0.0036 = 0.11988 GJ/kg). The old 0.113745 was ~5.4% low and overstated H2 mass demand, cost, storage, compression and credits.
2. IRA 45V | Removed from the base case. Behind an eligibility toggle; earned by the qualified H2 producer, capped at 10 years in the cashflow (was applied ~50 yrs to the end user).
3. LCFS | Removed from the base case. Behind an eligibility toggle; eligible price repriced to CARB-recent ~$66/tCO2e (was $150). Stationary CHP/kiln/transport eligibility must be documented before use.
4. Offtake revenue | The $4/kg H2 'production revenue' is OFF in the base case for end uses (a consumer cannot pay for H2 and also book production revenue). Use incremental NPV / avoided-cost framing.
5. CCS | Now an explicit on/off option (default OFF). Previously CCS cost was charged in EVERY scenario, including 0% H2, inflating LCOH.
6. Efficiency sign | Combustion efficiency rises slightly with H2 everywhere (Thermoflex); the Cashflow sheet previously used the opposite sign (a derate) vs the Fuel_Cost sheet.
7. Availability | LCOH now uses the SAME derived 50-yr mean availability as the cashflow (was a fixed 0.97 in LCOH vs ~0.955 derived in the cashflow).
8. LCOH at 0% | Shown as N/A (no hydrogen exists at 0% blend); removes the -$1.35/kg artefact at 0%.
9. Network units | TEA_Network total no longer adds $/kg layers to a $/MWh integration term; the stale cached total is refreshed on recalculation.
10. Incremental NPV | NPV_Comparison now reports NPV incremental to the 0% fossil baseline; the 0% incremental NPV is zero by construction. Absolute 'project' NPV is retained but flagged non-decision-grade.
Still preliminary / not rebuilt
Hydraulics / compressors | N_comp = MAX(1, distance/spacing x flow-factor) is a screening PROXY, not compressible pipeline hydraulics. It does not verify delivery pressure or compute compressor duty from pressure ratio. Do not treat compressor counts or the 3.1 kWh/kg adder as design values.
Reliability PoF | Component PoF are cumulative 'at least one functional failure' probabilities, NOT catastrophic integrity risk, and must not be read alongside rupture probability as equivalent consequence.
Lifecycle degradation | The lifecycle uses a CONSTANT hazard (exponential), not an age-dependent Weibull/renewal model, despite 'PoF rises with age' language. Residual-life claims are indicative only.
Pipe integrity | The FCGR step multipliers are a screening failure-rate multiplier model, NOT probabilistic fracture mechanics. 'Integrity saturates at 20%' is an artefact of the imposed step function, not a physical result.
CAPEX scaling | Pipeline $/mile, the $2M skid and compressor costs are not size/diameter/pressure/location-specific. Small low-utilisation loads (e.g. Fine Arts) show LCOH dominated by fixed-cost dilution, not technology cost.
Equipment limits | The 6.89-bar H2 partial-pressure rule is an API-617 centrifugal-compressor concern, not a universal component acceptance criterion. Replacement CAPEX should follow component-specific qualification.
Prices | H2 $2/kg is optimistic for clean delivered H2 (DOE ~$5-7/kg plant-gate); NG $4.74/GJ and electricity $0.235/kWh should be validated against actual bills/tariffs. Prices are screening placeholders.
Reconciliation | A separate SoCalGas workbook referenced by the review was not provided; only 4 workbooks + the dashboard are in this set. Report/dashboard/workbook reconciliation to a single engine remains outstanding.